## notes (hidden)
0
|  | 600 | 24 | 600 | 1000 | 0 | 0
|  | 800 | 30 | 800 | 1200 | 0 | 0
|  | 1000 | 36 | 1000 | 1400 | 0 | 0
|  | 1200 | 42 | 1200 | 1600 | 0 | 0
|  | 1400 | 48 | 1400 | 1800 | 0 | 0
|  | 1600 | 60 | 1600 | 2000 | 0 | 0
1800
2000
Total
| 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 58
|  |  |  | 65 | 75 | 80 | 85 | 90 | 95 | 105
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | #N/A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | #N/A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| #N/A | 0 |  | #N/A | #N/A
| #N/A | 0 |  | 0 | 0 |  |  | exactly
| #N/A | #N/A |  | 0 | 0 |  |  | x | y | err1 | err2 | err3 | ans
| #N/A | #N/A |  | 0 | 0 |  |  | y | y | 0 |  |  | 0
| #N/A | #N/A |  | #N/A |  |  |  | y | n |  |  |  | 0
| #N/A | #N/A | [5 empty] | n | n | #N/A | #N/A | #N/A | #N/A
0
sens |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 65 | 75 | 80 | 85 | 90 | 95 | 105
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | #N/A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | #N/A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| #N/A | 0 |  | #N/A | #N/A
| #N/A | 0 |  | 0 | 0 |  |  | exactly
| #N/A | #N/A |  | 0 | 0 |  |  | x | y | err1 | err2 | err3 | ans
| #N/A | #N/A |  | 0 | 0 |  |  | y | y | 0 |  |  | 0
| #N/A | #N/A |  | #N/A |  |  |  | y | n |  |  |  | 0
| #N/A | #N/A | [5 empty] | n | n | #N/A | #N/A | #N/A | #N/A
| #N/A | [11 empty] | 0

## Options (hidden)
PSH4BG

## Calcs (hidden)
Condenser :
ADP Evaporator:
|  |  | Condenser Entering Air Temperature: | 100 | (°F) Dry Bulb, 85°F to 115°F
|  |  | Evaporator Air Flow: | 1265 | CFM
|  |  | Entering Evaporator Air (DB): | 77.5 | (°F) Dry Bulb
|  |  | Entering Evaporator Air (WB): | 60.6 | (°F) Wet Bulb, 63°F to 71°F
Total
28.55 | 1200 60.6
| Diff 200 | 0.308 | Diff 1 cfm | 0.00154 | 1265 total | 28.4499
28.242 | 1400 60.6
Sens
25.32 | 1200 60.6
| Diff 200 | 0.5544 | Diff 1 cfm | 0.002772 | 1265 Sens | 25.1398
24.7656 | 1400 60.6

## PSH4BG_24 (hidden)
PSH4BG_24F_24
Evaporator Air |  | Condenser Entering Air Temperature ˚F
80 | °F DB | 65 |  | 75 |  | 80 |  | 85 |  | 90 |  | 95 |  | 105
CFM | EWB† ˚F | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh
|  | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens.
[16 empty] | Total Factors | [6 empty] | Sens. % | [6 empty] | IDB Adj | [6 empty] | Sens Calc
700 | 72 | 29.9613 | 14.0226 | 28.9161 | 13.5871 | 28.3065 | 13.3694 | 27.6968 | 13.1516 | 27 | 12.9339 | 26.3032 | 12.7161 | 24.8226 | 12.1935 | 1.233 | 1.19 | 1.1649 | 1.1398 | 1.1111 | 1.0824 | 1.0215 | 46.8% | 46.99% | 47.23% | 47.48% | 47.9% | 48.34% | 49.12% | 1.0286 | 0.94286 | 0.91429 | 0.88571 | 0.87143 | 0.85714 | 0.85714 | 14.0226 | 13.5871 | 13.3694 | 13.1516 | 12.9339 | 12.7161 | 12.1935
| 69.5 | 28.5677 | 15.5903 | 27.4355 | 15.1113 | 26.8258 | 14.8935 | 26.2161 | 14.6758 | 25.5847 | 14.4363 | 24.9532 | 14.1968 | 23.6032 | 13.7177 | 1.1756 | 1.129 | 1.1039 | 1.0789 | 1.0529 | 1.0269 | 0.97133 | 54.57% | 55.08% | 55.52% | 55.98% | 56.43% | 56.89% | 58.12% | 1.0286 | 0.94286 | 0.91429 | 0.88571 | 0.87143 | 0.85714 | 0.85714 | 15.5903 | 15.1113 | 14.8935 | 14.6758 | 14.4363 | 14.1968 | 13.7177
| 67 | 27.1742 | 17.1581 | 25.9548 | 16.6355 | 25.3452 | 16.4177 | 24.7355 | 16.2 | 24.1694 | 15.9387 | 23.6032 | 15.6774 | 22.3839 | 15.2419 | 1.1183 | 1.0681 | 1.043 | 1.0179 | 0.99462 | 0.97133 | 0.92115 | 63.14% | 64.09% | 64.78% | 65.49% | 65.95% | 66.42% | 68.09% | 1.0286 | 0.94286 | 0.91429 | 0.88571 | 0.87143 | 0.85714 | 0.85714 | 17.1581 | 16.6355 | 16.4177 | 16.2 | 15.9387 | 15.6774 | 15.2419
| 62 | 25.4323 | 20.4677 | 24.0387 | 19.8581 | 23.3855 | 19.5532 | 22.7323 | 19.2484 | 22.079 | 18.9435 | 21.4258 | 18.6387 | 20.1194 | 18.029 | 1.0466 | 0.98925 | 0.96237 | 0.93548 | 0.9086 | 0.88172 | 0.82796 | 80.48% | 82.61% | 83.61% | 84.67% | 85.8% | 86.99% | 89.61% | 1.0286 | 0.94286 | 0.91429 | 0.88571 | 0.87143 | 0.85714 | 0.85714 | 20.4677 | 19.8581 | 19.5532 | 19.2484 | 18.9435 | 18.6387 | 18.029
800 | 72 | 30.6581 | 14.7194 | 29.6129 | 14.371 | 28.9597 | 14.1532 | 28.3065 | 13.9355 | 27.6097 | 13.6742 | 26.9129 | 13.4129 | 25.3452 | 12.8903 | 1.2616 | 1.2186 | 1.1918 | 1.1649 | 1.1362 | 1.1075 | 1.043 | 48.01% | 48.53% | 48.87% | 49.23% | 49.53% | 49.84% | 50.86% | 1 | 0.925 | 0.9 | 0.875 | 0.85 | 0.825 | 0.825 | 14.7194 | 14.371 | 14.1532 | 13.9355 | 13.6742 | 13.4129 | 12.8903
| 69.5 | 29.3516 | 16.4613 | 28.2194 | 16.0258 | 27.5879 | 15.8081 | 26.9565 | 15.5903 | 26.2815 | 15.329 | 25.6065 | 15.0677 | 24.2129 | 14.5887 | 1.2079 | 1.1613 | 1.1353 | 1.1093 | 1.0815 | 1.0538 | 0.99642 | 56.08% | 56.79% | 57.3% | 57.84% | 58.33% | 58.84% | 60.25% | 1 | 0.925 | 0.9 | 0.875 | 0.85 | 0.825 | 0.825 | 16.4613 | 16.0258 | 15.8081 | 15.5903 | 15.329 | 15.0677 | 14.5887
| 67 | 28.0452 | 18.2032 | 26.8258 | 17.6806 | 26.2161 | 17.4629 | 25.6065 | 17.2452 | 24.9532 | 16.9839 | 24.3 | 16.7226 | 23.0806 | 16.2871 | 1.1541 | 1.1039 | 1.0789 | 1.0538 | 1.0269 | 1 | 0.94982 | 64.91% | 65.91% | 66.61% | 67.35% | 68.06% | 68.82% | 70.57% | 1 | 0.925 | 0.9 | 0.875 | 0.85 | 0.825 | 0.825 | 18.2032 | 17.6806 | 17.4629 | 17.2452 | 16.9839 | 16.7226 | 16.2871
| 62 | 26.3903 | 21.8613 | 24.9968 | 21.2516 | 24.3 | 20.9468 | 23.6032 | 20.6419 | 22.9065 | 20.2935 | 22.2097 | 19.9452 | 20.8161 | 19.2484 | 1.086 | 1.0287 | 1 | 0.97133 | 0.94265 | 0.91398 | 0.85663 | 82.84% | 85.02% | 86.2% | 87.45% | 88.59% | 89.8% | 92.47% | 1 | 0.925 | 0.9 | 0.875 | 0.85 | 0.825 | 0.825 | 21.8613 | 21.2516 | 20.9468 | 20.6419 | 20.2935 | 19.9452 | 19.2484
900 | 72 | 31.3548 | 15.4161 | 30.2226 | 15.0677 | 29.6129 | 14.85 | 29.0032 | 14.6323 | 28.2629 | 14.4145 | 27.5226 | 14.1968 | 25.8677 | 13.5871 | 1.2903 | 1.2437 | 1.2186 | 1.1935 | 1.1631 | 1.1326 | 1.0645 | 49.17% | 49.86% | 50.15% | 50.45% | 51% | 51.58% | 52.53% | 0.97778 | 0.91111 | 0.88889 | 0.86667 | 0.83333 | 0.8 | 0.8 | 15.4161 | 15.0677 | 14.85 | 14.6323 | 14.4145 | 14.1968 | 13.5871
| 69.5 | 30.2226 | 17.4194 | 29.1339 | 17.1145 | 28.546 | 16.8968 | 27.9581 | 16.679 | 27.2395 | 16.4395 | 26.521 | 16.2 | 24.8661 | 15.5468 | 1.2437 | 1.1989 | 1.1747 | 1.1505 | 1.121 | 1.0914 | 1.0233 | 57.64% | 58.74% | 59.19% | 59.66% | 60.35% | 61.08% | 62.52% | 0.97778 | 0.91111 | 0.88889 | 0.86667 | 0.83333 | 0.8 | 0.8 | 17.4194 | 17.1145 | 16.8968 | 16.679 | 16.4395 | 16.2 | 15.5468
| 67 | 29.0903 | 19.4226 | 28.0452 | 19.1613 | 27.479 | 18.9435 | 26.9129 | 18.7258 | 26.2161 | 18.4645 | 25.5194 | 18.2032 | 23.8645 | 17.5065 | 1.1971 | 1.1541 | 1.1308 | 1.1075 | 1.0789 | 1.0502 | 0.98208 | 66.77% | 68.32% | 68.94% | 69.58% | 70.43% | 71.33% | 73.36% | 0.97778 | 0.91111 | 0.88889 | 0.86667 | 0.83333 | 0.8 | 0.8 | 19.4226 | 19.1613 | 18.9435 | 18.7258 | 18.4645 | 18.2032 | 17.5065
| 62 | 25.1145 | 21.5038 | 23.757 | 20.8073 | 23.0782 | 20.5273 | 22.3994 | 20.2472 | 21.7885 | 19.9495 | 21.1777 | 19.6535 | 19.8201 | 19.0144 | 1.0335 | 0.97765 | 0.94972 | 0.92179 | 0.89665 | 0.87151 | 0.81564 | 85.62% | 87.58% | 88.95% | 90.39% | 91.56% | 92.8% | 95.93% | 0.97778 | 0.91111 | 0.88889 | 0.86667 | 0.83333 | 0.8 | 0.8 | 21.5038 | 20.8073 | 20.5273 | 20.2472 | 19.9495 | 19.6535 | 19.0144

## PSH4BG_36 (hidden)
CSA4BF_36
Evaporator Air |  | Condenser Entering Air Temperature ˚F
80 | °F DB | 65 |  | 75 |  | 80 |  | 85 |  | 90 |  | 95 |  | 105
CFM | EWB† ˚F | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh
|  | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens.
[16 empty] | Total Factors | [6 empty] | Sens. % | [6 empty] | IDB Adj | [6 empty] | Sens Calc
1050 | 72 | 27.8254 | 13.2202 | 27.9513 | 13.472 | 27.6995 | 13.4091 | 27.4477 | 13.3461 | 26.9126 | 13.1573 | 26.3775 | 12.9684 | 24.6148 | 12.2759 | 1.1451 | 1.1503 | 1.1399 | 1.1295 | 1.1075 | 1.0855 | 1.013 | 47.51% | 48.2% | 48.41% | 48.62% | 48.89% | 49.16% | 49.87% | 1.0667 | 1.0857 | 1.0762 | 1.0667 | 1.0381 | 1.0095 | 0.93333 | 13.2202 | 13.472 | 13.4091 | 13.3461 | 13.1573 | 12.9684 | 12.2759
| 69.5 | 27.1959 | 15.1718 | 26.9755 | 15.2032 | 26.6293 | 15.0931 | 26.283 | 14.9829 | 25.685 | 14.7626 | 25.0869 | 14.5422 | 23.3872 | 13.8497 | 1.1192 | 1.1101 | 1.0959 | 1.0816 | 1.057 | 1.0324 | 0.96244 | 55.79% | 56.36% | 56.68% | 57.01% | 57.48% | 57.97% | 59.22% | 1.0667 | 1.0857 | 1.0762 | 1.0667 | 1.0381 | 1.0095 | 0.93333 | 15.1718 | 15.2032 | 15.0931 | 14.9829 | 14.7626 | 14.5422 | 13.8497
| 67 | 26.5663 | 17.1233 | 25.9997 | 16.9345 | 25.5591 | 16.7771 | 25.1184 | 16.6197 | 24.4574 | 16.3679 | 23.7964 | 16.1161 | 22.1596 | 15.4236 | 1.0933 | 1.0699 | 1.0518 | 1.0337 | 1.0065 | 0.97927 | 0.91192 | 64.45% | 65.13% | 65.64% | 66.17% | 66.92% | 67.72% | 69.6% | 1.0667 | 1.0857 | 1.0762 | 1.0667 | 1.0381 | 1.0095 | 0.93333 | 17.1233 | 16.9345 | 16.7771 | 16.6197 | 16.3679 | 16.1161 | 15.4236
| 62 | 24.6148 | 20.6487 | 23.6705 | 20.208 | 23.1039 | 19.8933 | 22.5373 | 19.5785 | 21.9078 | 19.2008 | 21.2782 | 18.8231 | 19.8933 | 17.9417 | 1.013 | 0.97409 | 0.95078 | 0.92746 | 0.90155 | 0.87565 | 0.81865 | 83.89% | 85.37% | 86.1% | 86.87% | 87.64% | 88.46% | 90.19% | 1.0667 | 1.0857 | 1.0762 | 1.0667 | 1.0381 | 1.0095 | 0.93333 | 20.6487 | 20.208 | 19.8933 | 19.5785 | 19.2008 | 18.8231 | 17.9417
1200 | 72 | 27.7624 | 13.472 | 27.8883 | 13.6609 | 27.668 | 13.6609 | 27.4477 | 13.6609 | 26.9755 | 13.535 | 26.5034 | 13.4091 | 24.9295 | 12.9054 | 1.1425 | 1.1477 | 1.1386 | 1.1295 | 1.1101 | 1.0907 | 1.0259 | 48.53% | 48.98% | 49.37% | 49.77% | 50.18% | 50.59% | 51.77% | 0.96667 | 1 | 1 | 1 | 0.98333 | 0.96667 | 0.91667 | 13.472 | 13.6609 | 13.6609 | 13.6609 | 13.535 | 13.4091 | 12.9054
| 69.5 | 27.2588 | 15.581 | 27.1329 | 15.7383 | 26.8181 | 15.6911 | 26.5034 | 15.6439 | 25.9525 | 15.4708 | 25.4017 | 15.2977 | 23.7334 | 14.6681 | 1.1218 | 1.1166 | 1.1036 | 1.0907 | 1.068 | 1.0453 | 0.97668 | 57.16% | 58% | 58.51% | 59.03% | 59.61% | 60.22% | 61.8% | 0.96667 | 1 | 1 | 1 | 0.98333 | 0.96667 | 0.91667 | 15.581 | 15.7383 | 15.6911 | 15.6439 | 15.4708 | 15.2977 | 14.6681
| 67 | 26.7552 | 17.6899 | 26.3775 | 17.8158 | 25.9683 | 17.7214 | 25.5591 | 17.6269 | 24.9295 | 17.4066 | 24.3 | 17.1863 | 22.5373 | 16.4308 | 1.101 | 1.0855 | 1.0687 | 1.0518 | 1.0259 | 1 | 0.92746 | 66.12% | 67.54% | 68.24% | 68.97% | 69.82% | 70.73% | 72.91% | 0.96667 | 1 | 1 | 1 | 0.98333 | 0.96667 | 0.91667 | 17.6899 | 17.8158 | 17.7214 | 17.6269 | 17.4066 | 17.1863 | 16.4308
| 62 | 24.9925 | 21.5301 | 24.0482 | 21.2782 | 23.5131 | 21.0264 | 22.978 | 20.7746 | 22.3799 | 20.4284 | 21.7819 | 20.0821 | 20.3969 | 19.2008 | 1.0285 | 0.98964 | 0.96762 | 0.9456 | 0.92098 | 0.89637 | 0.83938 | 86.15% | 88.48% | 89.42% | 90.41% | 91.28% | 92.2% | 94.14% | 0.96667 | 1 | 1 | 1 | 0.98333 | 0.96667 | 0.91667 | 21.5301 | 21.2782 | 21.0264 | 20.7746 | 20.4284 | 20.0821 | 19.2008
1350 | 72 | 28.0142 | 13.9127 | 28.392 | 14.3534 | 28.2346 | 14.4163 | 28.0772 | 14.4793 | 27.5736 | 14.3534 | 27.0699 | 14.2275 | 25.3702 | 13.5979 | 1.1528 | 1.1684 | 1.1619 | 1.1554 | 1.1347 | 1.114 | 1.044 | 49.66% | 50.55% | 51.06% | 51.57% | 52.05% | 52.56% | 53.6% | 0.88889 | 0.91852 | 0.93333 | 0.94815 | 0.94815 | 0.94815 | 0.9037 | 13.9127 | 14.3534 | 14.4163 | 14.4793 | 14.3534 | 14.2275 | 13.5979
| 69.5 | 27.5106 | 16.0846 | 27.5736 | 16.5253 | 27.306 | 16.5567 | 27.0385 | 16.5882 | 26.4719 | 16.4308 | 25.9053 | 16.2734 | 24.1741 | 15.5495 | 1.1321 | 1.1347 | 1.1237 | 1.1127 | 1.0894 | 1.0661 | 0.99482 | 58.47% | 59.93% | 60.63% | 61.35% | 62.07% | 62.82% | 64.32% | 0.88889 | 0.91852 | 0.93333 | 0.94815 | 0.94815 | 0.94815 | 0.9037 | 16.0846 | 16.5253 | 16.5567 | 16.5882 | 16.4308 | 16.2734 | 15.5495
| 67 | 27.007 | 18.2565 | 26.7552 | 18.6972 | 26.3775 | 18.6972 | 25.9997 | 18.6972 | 25.3702 | 18.5083 | 24.7407 | 18.3194 | 22.978 | 17.501 | 1.1114 | 1.101 | 1.0855 | 1.0699 | 1.044 | 1.0181 | 0.9456 | 67.6% | 69.88% | 70.88% | 71.91% | 72.95% | 74.05% | 76.16% | 0.88889 | 0.91852 | 0.93333 | 0.94815 | 0.94815 | 0.94815 | 0.9037 | 18.2565 | 18.6972 | 18.6972 | 18.6972 | 18.5083 | 18.3194 | 17.501
| 62 | 25.3702 | 22.4114 | 24.4889 | 22.3484 | 23.9538 | 22.1911 | 23.4187 | 22.0337 | 22.8206 | 21.7189 | 22.2225 | 21.4041 | 20.8376 | 20.4598 | 1.044 | 1.0078 | 0.98575 | 0.96373 | 0.93912 | 0.91451 | 0.85751 | 88.34% | 91.26% | 92.64% | 94.09% | 95.17% | 96.32% | 98.19% | 0.88889 | 0.91852 | 0.93333 | 0.94815 | 0.94815 | 0.94815 | 0.9037 | 22.4114 | 22.3484 | 22.1911 | 22.0337 | 21.7189 | 21.4041 | 20.4598

## PSH4BG_48 (hidden)
CSA4BF_48
Evaporator Air |  | Condenser Entering Air Temperature ˚F
80 | °F DB | 65 |  | 75 |  | 80 |  | 85 |  | 90 |  | 95 |  | 105
CFM | EWB† ˚F | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh
|  | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens.
[16 empty] | Total Factors | [6 empty] | Sens. % | [6 empty] | IDB Adj | [6 empty] | Sens Calc
1200 | 72 | 28.3966 | 13.3603 | 27.9776 | 13.1741 | 27.5353 | 13.0112 | 27.0931 | 12.8483 | 26.4181 | 12.6155 | 25.7431 | 12.3828 | 23.9276 | 11.731 | 1.1686 | 1.1513 | 1.1331 | 1.1149 | 1.0872 | 1.0594 | 0.98467 | 47.05% | 47.09% | 47.25% | 47.42% | 47.75% | 48.1% | 49.03% | 0.83333 | 0.85 | 0.86667 | 0.88333 | 0.89167 | 0.9 | 0.95 | 13.3603 | 13.1741 | 13.0112 | 12.8483 | 12.6155 | 12.3828 | 11.731
| 69.5 | 27.6517 | 15.106 | 27.1397 | 14.9431 | 26.6974 | 14.7802 | 26.2552 | 14.6172 | 25.6034 | 14.3728 | 24.9517 | 14.1284 | 23.2526 | 13.4069 | 1.1379 | 1.1169 | 1.0987 | 1.0805 | 1.0536 | 1.0268 | 0.9569 | 54.63% | 55.06% | 55.36% | 55.67% | 56.14% | 56.62% | 57.66% | 0.83333 | 0.85 | 0.86667 | 0.88333 | 0.89167 | 0.9 | 0.95 | 15.106 | 14.9431 | 14.7802 | 14.6172 | 14.3728 | 14.1284 | 13.4069
| 67 | 26.9069 | 16.8517 | 26.3017 | 16.7121 | 25.8595 | 16.5491 | 25.4172 | 16.3862 | 24.7888 | 16.1302 | 24.1603 | 15.8741 | 22.5776 | 15.0828 | 1.1073 | 1.0824 | 1.0642 | 1.046 | 1.0201 | 0.99425 | 0.92912 | 62.63% | 63.54% | 64% | 64.47% | 65.07% | 65.7% | 66.8% | 0.83333 | 0.85 | 0.86667 | 0.88333 | 0.89167 | 0.9 | 0.95 | 16.8517 | 16.7121 | 16.5491 | 16.3862 | 16.1302 | 15.8741 | 15.0828
| 62 | 24.3466 | 19.2259 | 23.2293 | 18.7603 | 22.7172 | 18.5043 | 22.2052 | 18.2483 | 21.7397 | 17.9922 | 21.2741 | 17.7362 | 20.4362 | 17.2241 | 1.0019 | 0.95594 | 0.93487 | 0.91379 | 0.89464 | 0.87548 | 0.841 | 78.97% | 80.76% | 81.45% | 82.18% | 82.76% | 83.37% | 84.28% | 0.83333 | 0.85 | 0.86667 | 0.88333 | 0.89167 | 0.9 | 0.95 | 19.2259 | 18.7603 | 18.5043 | 18.2483 | 17.9922 | 17.7362 | 17.2241
1350 | 72 | 28.5828 | 13.7328 | 28.3966 | 13.6397 | 28.0241 | 13.5233 | 27.6517 | 13.4069 | 26.9767 | 13.1741 | 26.3017 | 12.9414 | 24.3931 | 12.2431 | 1.1762 | 1.1686 | 1.1533 | 1.1379 | 1.1102 | 1.0824 | 1.0038 | 48.05% | 48.03% | 48.26% | 48.48% | 48.84% | 49.2% | 50.19% | 0.87407 | 0.87407 | 0.88148 | 0.88889 | 0.88889 | 0.88889 | 0.88889 | 13.7328 | 13.6397 | 13.5233 | 13.4069 | 13.1741 | 12.9414 | 12.2431
| 69.5 | 27.7681 | 15.5017 | 27.3957 | 15.4086 | 26.9884 | 15.2806 | 26.581 | 15.1526 | 25.9409 | 14.8966 | 25.3009 | 14.6405 | 23.5784 | 13.919 | 1.1427 | 1.1274 | 1.1106 | 1.0939 | 1.0675 | 1.0412 | 0.97031 | 55.83% | 56.24% | 56.62% | 57.01% | 57.42% | 57.87% | 59.03% | 0.87407 | 0.87407 | 0.88148 | 0.88889 | 0.88889 | 0.88889 | 0.88889 | 15.5017 | 15.4086 | 15.2806 | 15.1526 | 14.8966 | 14.6405 | 13.919
| 67 | 26.9534 | 17.2707 | 26.3948 | 17.1776 | 25.9526 | 17.0379 | 25.5103 | 16.8983 | 24.9052 | 16.619 | 24.3 | 16.3397 | 22.7638 | 15.5948 | 1.1092 | 1.0862 | 1.068 | 1.0498 | 1.0249 | 1 | 0.93678 | 64.08% | 65.08% | 65.65% | 66.24% | 66.73% | 67.24% | 68.51% | 0.87407 | 0.87407 | 0.88148 | 0.88889 | 0.88889 | 0.88889 | 0.88889 | 17.2707 | 17.1776 | 17.0379 | 16.8983 | 16.619 | 16.3397 | 15.5948
| 62 | 25.0914 | 20.5293 | 24.0207 | 20.0172 | 23.4621 | 19.7379 | 22.9034 | 19.4586 | 22.3448 | 19.156 | 21.7862 | 18.8534 | 20.6224 | 18.2017 | 1.0326 | 0.98851 | 0.96552 | 0.94253 | 0.91954 | 0.89655 | 0.84866 | 81.82% | 83.33% | 84.13% | 84.96% | 85.73% | 86.54% | 88.26% | 0.87407 | 0.87407 | 0.88148 | 0.88889 | 0.88889 | 0.88889 | 0.88889 | 20.5293 | 20.0172 | 19.7379 | 19.4586 | 19.156 | 18.8534 | 18.2017
1500 | 72 | 28.769 | 14.1052 | 28.8155 | 14.1983 | 28.4897 | 14.1052 | 28.1638 | 14.0121 | 27.5121 | 13.756 | 26.8603 | 13.5 | 24.8121 | 12.7086 | 1.1839 | 1.1858 | 1.1724 | 1.159 | 1.1322 | 1.1054 | 1.0211 | 49.03% | 49.27% | 49.51% | 49.75% | 50% | 50.26% | 51.22% | 0.89333 | 0.90667 | 0.90667 | 0.90667 | 0.89333 | 0.88 | 0.81333 | 14.1052 | 14.1983 | 14.1052 | 14.0121 | 13.756 | 13.5 | 12.7086
| 69.5 | 27.9078 | 15.9207 | 27.675 | 15.9207 | 27.2909 | 15.8043 | 26.9069 | 15.6879 | 26.2784 | 15.4319 | 25.65 | 15.1759 | 23.881 | 14.3845 | 1.1485 | 1.1389 | 1.1231 | 1.1073 | 1.0814 | 1.0556 | 0.98276 | 57.05% | 57.53% | 57.91% | 58.3% | 58.72% | 59.17% | 60.23% | 0.89333 | 0.90667 | 0.90667 | 0.90667 | 0.89333 | 0.88 | 0.81333 | 15.9207 | 15.9207 | 15.8043 | 15.6879 | 15.4319 | 15.1759 | 14.3845
| 67 | 27.0466 | 17.7362 | 26.5345 | 17.6431 | 26.0922 | 17.5034 | 25.65 | 17.3638 | 25.0448 | 17.1078 | 24.4397 | 16.8517 | 22.95 | 16.0603 | 1.113 | 1.092 | 1.0738 | 1.0556 | 1.0307 | 1.0057 | 0.94444 | 65.58% | 66.49% | 67.08% | 67.7% | 68.31% | 68.95% | 69.98% | 0.89333 | 0.90667 | 0.90667 | 0.90667 | 0.89333 | 0.88 | 0.81333 | 17.7362 | 17.6431 | 17.5034 | 17.3638 | 17.1078 | 16.8517 | 16.0603
| 62 | 25.8362 | 21.8328 | 24.7655 | 21.3207 | 24.1603 | 21.0181 | 23.5552 | 20.7155 | 22.9034 | 20.3664 | 22.2517 | 20.0172 | 20.8552 | 19.1328 | 1.0632 | 1.0192 | 0.99425 | 0.96935 | 0.94253 | 0.91571 | 0.85824 | 84.5% | 86.09% | 86.99% | 87.94% | 88.92% | 89.96% | 91.74% | 0.89333 | 0.90667 | 0.90667 | 0.90667 | 0.89333 | 0.88 | 0.81333 | 21.8328 | 21.3207 | 21.0181 | 20.7155 | 20.3664 | 20.0172 | 19.1328

## PSH4BG_60 (hidden)
CSA4BF_60
Evaporator Air |  | Condenser Entering Air Temperature ˚F
80 | °F DB | 65 |  | 75 |  | 80 |  | 85 |  | 90 |  | 95 |  | 105
CFM | EWB† ˚F | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh
|  | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens.
[16 empty] | Total Factors | [6 empty] | Sens. % | [6 empty] | IDB Adj | [6 empty] | Sens Calc
1350 | 72 | 27.2038 | 12.3792 | 27.2802 | 12.5703 | 27.0127 | 12.513 | 26.7453 | 12.4557 | 26.1913 | 12.2455 | 25.6373 | 12.0354 | 23.9179 | 11.3476 | 1.1195 | 1.1226 | 1.1116 | 1.1006 | 1.0778 | 1.055 | 0.98428 | 45.51% | 46.08% | 46.32% | 46.57% | 46.75% | 46.94% | 47.44% | 1.0074 | 0.96296 | 0.94815 | 0.93333 | 0.92593 | 0.91852 | 0.94815 | 12.3792 | 12.5703 | 12.513 | 12.4557 | 12.2455 | 12.0354 | 11.3476
| 69.5 | 26.4969 | 14.2132 | 26.4969 | 14.4042 | 26.2008 | 14.3374 | 25.9047 | 14.2705 | 25.3221 | 14.0222 | 24.7394 | 13.7738 | 22.9627 | 12.9333 | 1.0904 | 1.0904 | 1.0782 | 1.066 | 1.0421 | 1.0181 | 0.94497 | 53.64% | 54.36% | 54.72% | 55.09% | 55.38% | 55.68% | 56.32% | 1.0074 | 0.96296 | 0.94815 | 0.93333 | 0.92593 | 0.91852 | 0.94815 | 14.2132 | 14.4042 | 14.3374 | 14.2705 | 14.0222 | 13.7738 | 12.9333
| 67 | 25.7901 | 16.0472 | 25.7137 | 16.2382 | 25.3889 | 16.1618 | 25.0642 | 16.0854 | 24.4528 | 15.7988 | 23.8415 | 15.5123 | 22.0075 | 14.5189 | 1.0613 | 1.0582 | 1.0448 | 1.0314 | 1.0063 | 0.98113 | 0.90566 | 62.22% | 63.15% | 63.66% | 64.18% | 64.61% | 65.06% | 65.97% | 1.0074 | 0.96296 | 0.94815 | 0.93333 | 0.92593 | 0.91852 | 0.94815 | 16.0472 | 16.2382 | 16.1618 | 16.0854 | 15.7988 | 15.5123 | 14.5189
| 62 | 23.6887 | 18.8745 | 22.6571 | 18.3396 | 22.1413 | 18.0722 | 21.6255 | 17.8047 | 21.0906 | 17.5182 | 20.5557 | 17.2316 | 19.4476 | 16.6585 | 0.97484 | 0.93239 | 0.91116 | 0.88994 | 0.86792 | 0.84591 | 0.80031 | 79.68% | 80.94% | 81.62% | 82.33% | 83.06% | 83.83% | 85.66% | 1.0074 | 0.96296 | 0.94815 | 0.93333 | 0.92593 | 0.91852 | 0.94815 | 18.8745 | 18.3396 | 18.0722 | 17.8047 | 17.5182 | 17.2316 | 16.6585
1500 | 72 | 27.3948 | 13.0288 | 27.5476 | 12.9906 | 27.3184 | 12.895 | 27.0892 | 12.7995 | 26.5542 | 12.6085 | 26.0193 | 12.4175 | 24.3 | 11.8061 | 1.1274 | 1.1336 | 1.1242 | 1.1148 | 1.0928 | 1.0708 | 1 | 47.56% | 47.16% | 47.2% | 47.25% | 47.48% | 47.72% | 48.58% | 1.0267 | 0.97333 | 0.96 | 0.94667 | 0.94 | 0.93333 | 0.94667 | 13.0288 | 12.9906 | 12.895 | 12.7995 | 12.6085 | 12.4175 | 11.8061
| 69.5 | 26.7835 | 14.8054 | 26.8599 | 14.8436 | 26.5925 | 14.7481 | 26.325 | 14.6526 | 25.7423 | 14.4233 | 25.1597 | 14.1941 | 23.383 | 13.4682 | 1.1022 | 1.1053 | 1.0943 | 1.0833 | 1.0594 | 1.0354 | 0.96226 | 55.28% | 55.26% | 55.46% | 55.66% | 56.03% | 56.42% | 57.6% | 1.0267 | 0.97333 | 0.96 | 0.94667 | 0.94 | 0.93333 | 0.94667 | 14.8054 | 14.8436 | 14.7481 | 14.6526 | 14.4233 | 14.1941 | 13.4682
| 67 | 26.1722 | 16.5821 | 26.1722 | 16.6967 | 25.8665 | 16.6012 | 25.5608 | 16.5057 | 24.9304 | 16.2382 | 24.3 | 15.9708 | 22.466 | 15.1302 | 1.077 | 1.077 | 1.0645 | 1.0519 | 1.0259 | 1 | 0.92453 | 63.36% | 63.8% | 64.18% | 64.57% | 65.13% | 65.72% | 67.35% | 1.0267 | 0.97333 | 0.96 | 0.94667 | 0.94 | 0.93333 | 0.94667 | 16.5821 | 16.6967 | 16.6012 | 16.5057 | 16.2382 | 15.9708 | 15.1302
| 62 | 24.1472 | 19.7915 | 23.1538 | 19.2948 | 22.6189 | 19.0465 | 22.084 | 18.7981 | 21.53 | 18.5116 | 20.9759 | 18.225 | 19.7915 | 17.5755 | 0.99371 | 0.95283 | 0.93082 | 0.90881 | 0.88601 | 0.86321 | 0.81447 | 81.96% | 83.33% | 84.21% | 85.12% | 85.98% | 86.89% | 88.8% | 1.0267 | 0.97333 | 0.96 | 0.94667 | 0.94 | 0.93333 | 0.94667 | 19.7915 | 19.2948 | 19.0465 | 18.7981 | 18.5116 | 18.225 | 17.5755
1650 | 72 | 27.5476 | 13.2962 | 27.8151 | 13.3726 | 27.6241 | 13.3153 | 27.433 | 13.258 | 26.9172 | 13.0861 | 26.4014 | 12.9142 | 24.6821 | 12.3028 | 1.1336 | 1.1447 | 1.1368 | 1.1289 | 1.1077 | 1.0865 | 1.0157 | 48.27% | 48.08% | 48.2% | 48.33% | 48.62% | 48.91% | 49.85% | 1.0182 | 0.98182 | 0.9697 | 0.95758 | 0.95152 | 0.94545 | 0.93333 | 13.2962 | 13.3726 | 13.3153 | 13.258 | 13.0861 | 12.9142 | 12.3028
| 69.5 | 27.0509 | 15.283 | 27.2229 | 15.4167 | 26.9841 | 15.3499 | 26.7453 | 15.283 | 26.1722 | 15.0633 | 25.5991 | 14.8436 | 23.8033 | 14.0795 | 1.1132 | 1.1203 | 1.1105 | 1.1006 | 1.077 | 1.0535 | 0.97956 | 56.5% | 56.63% | 56.88% | 57.14% | 57.55% | 57.99% | 59.15% | 1.0182 | 0.98182 | 0.9697 | 0.95758 | 0.95152 | 0.94545 | 0.93333 | 15.283 | 15.4167 | 15.3499 | 15.283 | 15.0633 | 14.8436 | 14.0795
| 67 | 26.5542 | 17.2698 | 26.6307 | 17.4608 | 26.3441 | 17.3844 | 26.0575 | 17.308 | 25.4271 | 17.0406 | 24.7967 | 16.7731 | 22.9245 | 15.8561 | 1.0928 | 1.0959 | 1.0841 | 1.0723 | 1.0464 | 1.0204 | 0.9434 | 65.04% | 65.57% | 65.99% | 66.42% | 67.02% | 67.64% | 69.17% | 1.0182 | 0.98182 | 0.9697 | 0.95758 | 0.95152 | 0.94545 | 0.93333 | 17.2698 | 17.4608 | 17.3844 | 17.308 | 17.0406 | 16.7731 | 15.8561
| 62 | 24.5675 | 20.7085 | 23.6123 | 20.2882 | 23.0774 | 20.0399 | 22.5425 | 19.7915 | 21.9693 | 19.505 | 21.3962 | 19.2184 | 20.1354 | 18.4925 | 1.011 | 0.9717 | 0.94969 | 0.92767 | 0.90409 | 0.8805 | 0.82862 | 84.29% | 85.92% | 86.84% | 87.8% | 88.78% | 89.82% | 91.84% | 1.0182 | 0.98182 | 0.9697 | 0.95758 | 0.95152 | 0.94545 | 0.93333 | 20.7085 | 20.2882 | 20.0399 | 19.7915 | 19.505 | 19.2184 | 18.4925

## Form (hidden)
|  | Select Maytag Condenser: | [6 empty] | Second Stage (Boost Speed C5) Cooling
|  | ADP Evaporator: | [10 empty] | 24
|  | Nominal Capacity: |  | (Mbtuh) | [6 empty] | Condenser Entering Air Temperature: |  | (°F) Dry Bulb, 65°F to 105°F
|  | AHRI Rated Capacity: |  | (Mbtuh) @ 95 ˚F & 80/67 ˚F conditions | [6 empty] | Evaporator Air Flow (CFM): |  |  | to
|  | Entering Evaporator Air (DB): |  | (°F) Dry Bulb -- 80°F Standard | [6 empty] | Entering Evaporator Air (WB): |  | (°F) Wet Bulb, 62°F to 72°F
48
CFM
Extended Ratings
Maytag Condenser :
ADP Evaporator:
[5 empty] | Condenser Entering Air Temperature: |  | (°F) Dry Bulb, 65°F to 105°F
[5 empty] | Evaporator Air Flow: |  | CFM
[5 empty] | Entering Evaporator Air (DB): |  | (°F) Dry Bulb
[5 empty] | Entering Evaporator Air (WB): |  | (°F) Wet Bulb, 62°F to 72°F
[5 empty] | AHRI Rated Capacity: |  | (Mbtuh) @ 95 ˚F & 80/67 ˚F conditions
Evaporator Air |  | Condenser Entering Air Temperature ˚F
80 | °F DB | 65 |  | 75 |  | 80 |  | 85 |  | 90 |  | 95 |  | 105
CFM | EWB† ˚F | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh |  | Capacity Mbtuh
|  | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens. | Total | Sens.
|  |  | Condenser Entering Air Temperature: |  | (°F) Dry Bulb, 65°F to 105°F |  |  |  | CAPACITY IN MBTUH UNDER SPECIFIC CONDITIONS LISTED
|  |  | Evaporator Air Flow: |  | CFM |  |  |  |  | TOTAL
|  |  | Entering Evaporator Air (WB): |  | (°F) Wet Bulb, 62°F to 72°F |  |  |  |  | SENSIBLE
Second Stage (Boost Speed C5) Cooling
Notes: | † Entering Wet Bulb
Extended ratings are not certified. They are calculated based upon typical condenser performance curves and are for engineering information only.
When the required data fall between the published data, interpolation may be performed. Extrapolation is not an acceptable practice.
Displayed sensible capacity has been adjusted based upon indoor DB. Sensible capacity will increase with higher indoor DB and decrease with lower indoor DB.
The magnitude of the adjustment depends partially on evaporator air flow, with greater adjustment at higher CFM.
Printed: | [14 empty] | M-19-A
For use by ADP Customers only.
Copyright 2010-2016
Version M-19-A

## Instructions (hidden)
This spreadsheet generates capacity information for ADP rated matches at other than nominal conditions.
The information is provided is not certified and is provided for engineering use only.
The latest version will allways be available at: www.adpnow.com/extratings/
In order to generate an extended rating, you will need the following information:
Condenser model number
ADP coil model number
Nominal capacity
Rated capacity (from AHRI database)
Condenser entering air dry bulb temperature
Indoor entering air dry bulb temperature
Indoor entering air wet bulb temperature
Indoor airflow
Select the condenser series and nominal tonnage form the drop down lists.
Enter the remaining information in the correct cells. Note there are limits on the range of values allowed.
Click on "Calculate" to calculate the extended ratings.
The table will show capacities for various conditions. The capacities at the specific design point are
at the bottom of the page.
From this point you may:
Click "Clear" to clear the form and start over.
Click "Print" to print a copy of the data.
Click "Copy" to copy the data to a new spreadsheet and save it in the same directory.
Notes: | Displayed sensible capacity has been adjusted based upon indoor DB. Sensible capacity will
increase with higher indoor DB and decrease with lower indoor DB. The magnitude of the
adjustment depends partially on evaporator air flow, with greater adjustment at higher CFM.
Versions: | M-14-A | 2014-05-27 | Initial public release
| M-15-A | 2015-01-31 | Renewed date key through 2015
| M-16-A | 2016-03-22 | Renewed date key through 2016
| M-19-A | 2019-05-20 | New Version

## Prompt
In order to use this spreadsheet,
Please enable Macros in your security settings.
Enabling Macros in Excel 2007
1. In Excel, click the Office button in the upper left corner of the screen.
2. Click the "Excel Options" button in the lower right.
3. Click the "Trust Center" button on the left. Then, at the bottom right, select "Trust Center Settings" as shown below.
4. In the next window, select "Macro Settings," then select the radio button for "Disable all macros with notification."
5. When openning this spreadsheet, you will see a warning like this in the menu bar:
6. Select "Enable this content" and click "Okay". The spreadsheet will now be functional.