## Instructions
UNIT HEATER SIZING GUIDE
Instructions
1 | Print the tab that says "Table 1 and Tables 2-4". You will need to refer to them.
Wall and Ceiling:
2 | Inside Temp. - enter the inside temperature you would like to maintain.
3 | Outside Temp. - enter the outside temp, based on table 1. This will be based on the location of the building.
Floor:
4 | Inside Temp. - enter the inside temperature you would like to maintain.
5 | Ground Temp - enter the ground temp, based on table 2.
Building Dimensions:
Enter the length, width and height of the building to determine the volume (Cubic feet).
Construction "U" Values:
Enter the "U" values for the walls, roof, floor, windows and doors, based on table 3.
Please note: For additional types of construction, refer to the ASHRAE Handbook of Fundamentals.
Calculations:
Enter the number of doors, along with the height and width.
Enter the same information for the windows, if any.
Infiltration:
See table 4, for air changes.
At the bottom of the page you will see the total BTU/HR needed for this building.
To determine which unit heater and how many, you will need please refer to the "unit heater model" page.
X
X

## Form
UNIT HEATER SIZING GUIDE
Job Name: | [14 empty] | Contact:
City & State: | [14 empty] | Phone:
Building Use: | [14 empty] | Email:
Distributor: | [14 empty] | Contact:
Branch: | [14 empty] | Phone:
City & State: | [14 empty] | Email:
Design Temperature Differentials: | [14 empty] | Date:
Wall & Ceiling: (°F) | [16 empty] | Floor: (°F)
Inside Temp. | [7 empty] | 60 | [8 empty] | Inside Temp. | [6 empty] | 60
Outside Temp. (table 2) | [7 empty] | 6 | [8 empty] | Ground Temp. (table 3) | [6 empty] | 50
Design Temp. Diff. | [6 empty] | = | 54 | [8 empty] | Design Temp. Diff. | [5 empty] | = | 10
Building Information:
Dimensions: (ft.)
Length |  | 30 |  |  |  | X | Width |  | 30 |  |  |  | X | Height |  | 10 |  |  | = | Volume (cu.ft.) |  |  |  | 9000
Construction "U" Values: (table 1) | [19 empty] | Infiltration: (table 4)
Walls |  |  | 0.08 |  |  |  | Roof |  | 0.08 |  |  |  | Floor |  | 0.65 |  |  |  |  | Air changes |  |  |  | 1.5
Windows | [6 empty] | Doors |  | 1.2 | [10 empty] | Exhaust (CFM)
Calculations:
Doors: |  |  |  |  | (ft.) |  |  |  | (ft.) |  |  | Area (sq. ft.) |  |  |  |  | "U" Factor |  |  | Design T.D. |  |  | BTU/HR
# | 1 |  | X | H | 7 |  | X | W | 3 |  | = |  | 21 |  |  | X | 1.2 |  | X | 54 |  | = | 1360.8
# | 1 |  | X | H | 10 |  | X | W | 10 |  | = | 1 | 100 |  |  | X | 1.2 |  | X | 54 |  | = | 6480
# |  |  | X | H |  |  | X | W |  |  | = |  | 0 |  |  | X | 1.2 |  | X | 54 |  | = | 0
Windows:
# |  |  | X | H |  |  | X | W |  |  | = |  | 0 |  |  | X | 0 |  | X | 54 |  | = | 0
# |  |  | X | H |  |  | X | W |  |  | = | 2 | 0 |  |  | X | 0 |  | X | 54 |  | = | 0
# |  |  | X | H |  |  | X | W |  |  | = |  | 0 |  |  | X | 0 |  | X | 54 |  | = | 0
Walls:
L | 30 |  | X | H | 10 |  | X | 2 | - | 1 | = | 3 | 479 |  |  | X | 0.08 |  | X | 54 |  | = | 2069.28
W | 30 |  | X | H | 10 |  | X | 2 | - | 2 | = | 4 | 600 |  |  | X | 0.08 |  | X | 54 |  | = | 2592
Floor:
L | 30 |  | X | W | 30 | [5 empty] | = | 5 | 900 |  |  | X | 0.65 |  | X | 10 |  | = | 5850
Roof:
L | 30 |  | X | W | 30 | [5 empty] | = | 6 | 900 |  |  | X | 0.08 |  | X | 54 |  | = | 3888
Infiltration: |  |  |  | Max of |  | Air changes |  |  | 1.5 | X | Volume |  | 9000 |  | = | 13500 |  | X | TD | 54 | / 55 | = | 13254.5455
[6 empty] | Exhaust CFM |  |  | 0 |  | X | Min/hr |  | 60 | = | 0
[18 empty] | Subtotal |  |  |  | = | 35494.6255
Add 10% for possible high winds, morning warm ups, | [17 empty] | Safety Factor |  |  |  | = | 3549.4625
periods of higher than average infiltration etc.
[18 empty] | Total BTU/HR |  |  |  | = | 39044.088
All calculations are based on information received from the customer (bold boxes).

## Table 1
Table 1
COMMON BUILDING MATERIALS |  | U" | COMMON BUILDING MATERIALS |  | "U"
Walls: |  |  | Flat Roofs:
Poured concrete, 80#/cu.ft. |  |  | Corrugated Metal (un-insulated) ................................ |  | 1.50
| 8-inch............................................................... | 0.25 |  | w/1-inch bolt or blanket ............................ | 0.23
| 12-inch............................................................. | 0.18 |  | w/1 1/2-inch bolt or blanket ...................... | 0.16
Concrete Block, hollow cinder aggregate |  |  |  | w/3-inch bolt or blanket ............................ | 0.08
| 8-inch............................................................... | 0.39 | Flat Metal
| 12-inch............................................................. | 0.36 |  | w/3/8-inch built-up roofing ....................... | 0.90
Concrete Block, hollow gravel aggregate |  |  |  | w/1-inch blanket insulation under deck .... | 0.21
| 8-inch............................................................... | 0.52 |  | w/2-inch blanket insulation under deck .... | 0.12
| 12-inch............................................................. | 0.47 | Wood-1"
Concrete Block, w/4-inch facebrick |  |  |  | (un-insulated) w/3/8-inch built-up roofing . | 0.48
| 8-inch Cinder .................................................. | 0.33 |  | w/1-inch blanket insulation ....................... | 0.17
| 8-inch Gravel .................................................. | 0.41 | Wood-2"
Metal |  |  |  | (un-insulated) w/3/8-inch built-up roofing . | 0.32
| (un-insulated) ................................................. | 1.17 |  | w/1-inch blanket insulation ....................... | 0.15
| w/1-inch blanket insulation ............................. | 0.22 | Pitched Roofs:
| w/3-inch blanket insulation ............................. | 0.08 | Corrugated Metal (un-insulated) .................................. |  | 1.50
Frame |  |  |  | w/1-inch bolt or blanket ............................ | 0.23
| 2x4 w/ 1/2" asphalt sheathing and wood |  |  | w/1 1/2-inch bolt or blanket ...................... | 0.16
| siding, 1/2" sheetrock |  |  | w/3-inch bolt or blanket ............................ | 0.08
| (un-insulated) ................................................. | 0.23 | Framed Roof (un-insulated) ........................................ |  | 0.48
| w/3-inch insulation .......................................... | 0.08 |  | w/R-11 (3 1/2") Fiberglas ......................... | 0.09
Windows: |  |  |  | w/R-19 (6") Fiberglas ............................... | 0.05
| Vertical, single-glass ....................................... | 1.13 |  | w/1" Polystyrene ...................................... | 0.14
| Vertical, double-glass ..................................... | 0.69 | Floors:
| Horizontal, single-glass (sky light) .................. | 1.40 |  | 4-inch concrete ......................................... | 0.65
Doors: |  |  |  | 6-inch concrete ......................................... | 0.43
| Metal-single sheet .......................................... | 1.20 |  | 8-inch concrete ......................................... | 0.33
| Wood, 1-inch .................................................. | 0.64 |  | 10-inch concrete ....................................... | 0.26
| Wood, 2-inch .................................................. | 0.43
Note: For additional types of construction, refer to the ASHRAE Handbook of Fundamentals.

## Tables 2-4
Table 2 | Winter Design Temperatures
STATE | CITY | TEMP F | STATE | CITY | TEMP F | STATE | CITY | TEMP F | STATE | CITY | TEMP F
Alabama | Birmingham | 21 | Illinois (cont) | Moline | -4 | Nebraska | Grand Island | -3 | Penn. (cont) | Scranton | 5
| Huntsville | 16 |  | Peoria | -4 |  | Lincoln | -2 |  | Williamsport | 7
| Mobile | 29 |  | Rockford | -4 |  | Norfolk | -4 | Rhode Island | Newport | 9
| Montgomery | 25 |  | Springfield | 2 |  | North Platte | -4 |  | Providence | 9
Alaska | Anchorage | -18 | Indiana | Evansville | 9 |  | Omaha | -3 | S. Carolina | Charleston | 27
| Fairbanks | -47 |  | Fort Wayne | 1 |  | Scottsbluff | -3 |  | Columbia | 24
| Juneau | 1 |  | Indianapolis | 2 | Nevada | Elko | -2 |  | Florence | 25
| Nome | -27 |  | South Bend | 1 |  | Ely | -4 |  | Greenville | 22
Arizona | Flagstaff | 4 | Iowa | Burlington | -3 |  | Las Vegas | 28 | S. Dakota | Huron | -14
| Pheonix | 34 |  | Des Moines | -5 |  | Reno | 10 |  | Rapid City | -7
| Tucson | 32 |  | Dubuque | -7 |  | Winnemucca | 3 |  | Sioux Falls | -11
| Winslow | 10 |  | Sioux City | -7 | N. Hamp. | Concord | -3 | Tennessee | Bristol | 14
| Yuma | 39 |  | Waterloo | -10 |  | Portsmouth | 2 |  | Chattanooga | 18
Arkansas | Fort Smith | 17 | Kansas | Dodge City | 5 | N. Jersey | Atlantic City | 13 |  | Knoxville | 19
| Little Rock | 20 |  | Goodland | 0 |  | Newark | 14 |  | Memphis | 18
| Texarkana | 23 |  | Topeka | 4 |  | Trenton | 14 |  | Nashville | 14
California | Bakersfield | 32 |  | Wichita | 7 | N. Mexico | Albuquerque | 16 | Texas | Abilene | 20
| Burbank | 39 | Kentucky | Covington | 6 |  | Raton | 1 |  | Amarillo | 11
| Fresno | 30 |  | Lexington | 8 |  | Roswell | 18 |  | Austin | 28
| Long Beach | 43 |  | Louisville | 10 |  | Silver City | 10 |  | Brownsville | 39
| Los Angeles | 40 | Louisiana | Alexandria | 27 | New York | Albany | -1 |  | Corpus Christi | 35
| Oakland | 36 |  | Baton Rouge | 29 |  | Binghamton | 1 |  | Dallas | 22
| Sacramento | 32 |  | Lake Charles | 31 |  | Buffalo | 6 |  | El Paso | 24
| San Diego | 44 |  | New Orleans | 33 |  | New York | 15 |  | Fort Worth | 22
| San Francisco | 38 |  | Shreveport | 25 |  | Rochester | 5 |  | Galveston | 36
| Santa Maria | 33 | Maine | Bangor | -6 |  | Schenectady | 1 |  | Houston | 32
Colorado | Alamosa | -16 |  | Caribou | -13 |  | Syracuse | 2 |  | Laredo | 36
| Colo. Springs | 2 |  | Portland | -1 | N. Carolina | Asheville | 14 |  | Lubbock | 15
| Denver | 1 | Maryland | Baltimore | 13 |  | Charlotte | 22 |  | Midland | 21
| Grand Junction | 7 |  | Frederich | 12 |  | Greensboro | 18 |  | Port Authur | 31
| Pueblo | 0 | Mass. | Boston | 9 |  | Raleigh | 20 |  | San Angelo | 22
Conn. | Bridgeport | 9 |  | Pittsfield | -3 |  | Wilmington | 26 |  | San Antonio | 30
| Hartford | 7 |  | Worcester | 4 |  | Winston-Salem | 20 |  | Victoria | 32
| New Haven | 7 | Michigan | Alpena | -6 | N. Dakota | Bismarck | -19 |  | Waco | 26
Delaware | Wilmington | 14 |  | Detroit | 6 |  | Devils Lake | -21 |  | Witchita Falls | 18
D.C. | Washington | 17 |  | Escanaba | -7 |  | Fargo | -18 | Utah | Ogden | 5
Florida | Daytona Beach | 35 |  | Flint | 1 |  | Williston | -21 |  | Provo | 6
| Fort Myers | 44 |  | Grand Rapids | 5 | Ohio | Akron | 6 |  | Salt Lake City | 8
| Jacksonville | 32 |  | Lansing | 1 |  | Cincinnati | 6 | Vermont | Burlington | -7
| Key West | 57 |  | Marquette | -8 |  | Cleveland | 5 |  | Rutland | -8
| Lakeland | 41 |  | Muskegon | 6 |  | Columbus | 5 | Virginia | Lynchburg | 16
| Miami | 47 |  | Saginaw | 4 |  | Dayton | 4 |  | Norfolk | 22
| Orlando | 38 |  | Sault Ste. Marie | -8 |  | Mansfield | 5 |  | Richmond | 17
| Pensacola | 29 | Minn. | Duluth | -16 |  | Sandusky | 6 |  | Roanoke | 16
| Tallahassee | 30 |  | Minneapolis | -12 |  | Toledo | 1 | Washington | Olympia | 22
| Tampa | 40 |  | Rochester | -12 |  | Youngstown | 4 |  | Seattle | 26
| W. Palm Beach | 45 | Miss. | Jackson | 25 | Oklahoma | Norman | 13 |  | Spokane | 2
Georgia | Athens | 22 |  | Meridan | 23 |  | Oklahoma City | 13 |  | Tacoma | 24
| Atlanta | 22 |  | Vicksburg | 26 |  | Tulsa | 13 |  | Walla Walla | 7
| Augusta | 23 | Missouri | Columbia | 4 | Oregon | Astoria | 29 |  | Yakima | 5
| Columbus | 24 |  | Kansas City | 6 |  | Eugene | 22 | W. Virginia | Charleston | 11
| Macon | 25 |  | St. Joseph | 2 |  | Medford | 23 |  | Elkins | 6
| Rome | 22 |  | St. Louis | 6 |  | Pendleton | 5 |  | Huntington | 10
| Savannah | 27 |  | Springfield | 9 |  | Portland | 23 |  | Parkersburg | 11
Hawaii | Honolulu | 63 | Montana | Billings | -10 |  | Roseburg | 23 | Wisconsin | Green Bay | -9
| Hilo | 62 |  | Glasgow | -18 |  | Salem | 23 |  | La Crosse | -9
Idaho | Boise | 10 |  | Great Falls | -15 | Penn. | Allentown | 9 |  | Madison | -7
| Lewiston | 6 |  | Havre | -11 |  | Erie | 9 |  | Milwaukee | -4
| Pocatello | -1 |  | Helena | -16 |  | Harrisburg | 11 | Wyoming | Casper | -5
Illinois | Aurora | -1 |  | Kalispell | -7 |  | Philadelphia | 14 |  | Cheyenne | -1
| Champaign | 2 |  | Miles City | -15 |  | Pittsburgh | 5 |  | Lander | -11
| Chicago | -4 |  | Missoula | -6 |  | Reading | 13 |  | Sheridan | -8
Table 3 |  |  |  |  | Table 4
Winter Design Temp. |  | Use Ground Temp. |  |  | Building Types | [5 empty] | Air Changes (per hr.)
Above +15F |  | Disregard Floor Load |  |  | Residential type building, good insulation,vapor barrier,little or no door openings. | [5 empty] | .75 - 1
0 to +15F |  | +60F |  |  | Warehouse, average insulation, little or no door openings | [5 empty] | 1 - 1.5
-20 to 0F |  | +50F |  |  | Commercial garage (auto care center) average insulation, many door openings. | [5 empty] | 1.5 - 2.5
-40 to -20F |  | +40F |  |  | Warehouse, poor insulation, many door openings | [5 empty] | 2 - 2.5
[5 empty] | Warehouse, poor insulation, doors left open sometimes. | [5 empty] | 2.5 - 4
NOTE: These figures are to be used as guidelines only. It is up to the job estimator to accurately determine the
number of air changes per hour the structure will experience.
If the space contains ventilating equipment, determine the total CFM exhausted. Use this figure in the following
formula.
BTUH = (CFM exhausted X T.D.)/ 55
If this Btuh is greater than the amount under infiltration, use this amount.